## Summary
Description | Total Amount
Original Assessment (2017) | 2539996.88
Updated Assessment (2021) | 810940.236
Assessment Total Remaining w/ Cost Share Included | 636722.3265
Priority Level | FCA Total | Total County Cost
Urgent (Immediate) | 37110.6 | 14487.4563
Urgent (1 Year) | 181293.908 | 151503.0315
Urgent (2-3 Years) | 277250.764 | 201502.9158
Near Term (4-7 Years) | 315284.964 | 269228.923
TOTAL | 810940.236 | 636722.3265
Fire Department | FCA Total | Total County Cost
282 Durham Highway Station #1 | 108592.548 | 108592.548
162 Fairview Fire Station #1 | 31194.78 | 31194.78
249 Fairview Station #2 | 472 | 472
262 Garner Station #1 | 60040.48 | 26868.1148
248 Garner Station #2 | 85080.864 | 38073.6866
295 Garner Station #3 | 32162.964 | 14392.9264
273 Hopkins Station #1 | 39577 | 39577
214 Eastern Wake Station #2 Hester St | 27564 | 14134.8192
281 Northern Wake Station # 3 | 19839.6 | 19839.6
280 Northern Wake Station # 4 | 86073.6 | 86073.6
163 Rolesville Station #1 | 72372 | 33500.9988
290 Swift Creek Station #1 | 13262.4 | 13262.4
278 Wake Forest Station #5 | 31200.4 | 7232.2527
275 Wake New Hope Station #2 | 70274.4 | 70274.4
271 Wendell Station #1 | 2000 | 2000
274 Wendell Station #2 | 93578.4 | 93578.4
164 Western Wake Station #1 | 37654.8 | 37654.8
TOTAL | 810940.236 | 636722.3265
Department Type | TOTAL
Non-Profit | 502519.528
Cost Share | 134202.7985

## Staff Recommendation FY23
# | Deficiency Information | [5 empty] | Full Deficiency Cost Estimate
[7 empty] | Total Estimated Cost for FY23 (20% Increase) | Total Cost w/ Cost Share for FY23 | Recommeneded for FY23 Budget
| Station | Cost Share | Type | Priority | Name | Description
1 | Garner 1 | 44.75% | Mechanical System | Urgent (Immediate) | Replace Indoor AHU Component for DX Split System 4 | Indoor air handler was observed to be in poor/unreliable condition at assessment inspection. Recommend immediate replacement of this component only due to poor life expectancy. | 2250 | 1006.875 | 1006.875
2 | Knightdale 1 | 51.28% | Architectural System | Urgent (Immediate) | Reinforce Center Stair Stringer Lap Connection | Reinforce Center Stair Stringer Lap Connection | 173 | 88.7144 | 88.7144
3 | Northern Wake 3 | N/A | Electrical System | Urgent (Immediate) | Exterior Lighting Fixtures - Original Renewal | Auto generated renewal for Exterior Lighting Fixtures - Original. System Description: Incandescent lights are at exterior doors. 1 can light in soffit. Pricing includes fixtures, wiring, and controls. | 4430 | N/A | 4430
4 | Northern Wake 4 | N/A | Electrical System | Urgent (Immediate) | Bay Lighting - Original HID and Linear Fluorescent Renewal | Auto generated renewal for Bay Lighting - Original HID and Linear Fluorescent. System Description: Pendant Round | 2536 | N/A | 2536
5 | Wake Forest 5 | 23.18% | Plumbing System | Urgent (Immediate) | Shower Discharges to Grade | Shower drain piping runs underground and discharges into ditch at rear of property. The discharge occurs at NE segment of ditch adjacent to the neighbor's property. Shower should be connected to main septic system. | 2722 | 630.87 | 630.87
6 | Wake Forest 5 | 23.18% | Plumbing System | Urgent (Immediate) | Septic System Renewal | Auto generated renewal for Septic System. System Description: System includes tank and leaching field. Septic field is insufficient and requires pumping every 60 days. Pumping this often isn't an efficient use of funds. Chief said septic field was compromised during the construction of Falls of Neuse Road. Recommend tying into municipal sewer. | 25000 | 5795 | 5795
7 | Durham Hwy 1 | N/A | Architectural Aesthetics | Urgent (1 Year) | Add Second means of Egress from Second Floor | Nine beds and a 1900 SF dayroom exist on the 2352 FS second floor. Code at time of construction allowed a single exit for Group B if less than 3500 sf and serving fewer than 40 person, and for R-1 with fewer than 4 dwelling units. Current Code required 2 exists if second floor occupant load is greater than 10. At 100 sf/person for Group B area plus none beds equals a current occupant load of 27. Although not mandatory a second exist is recommended to improve life safety. | 49894.02 | N/A | 49894.02
8 | Fairview 1 | N/A | Architectural Aesthetics | Urgent (1 Year) | Repair Quarry Tile Floor in Apparatus Bay | Quarry Tile system in apparatus bay 101 isexhibiting areas of breakage and loosening of tiles. Particular weak points were observed at overhead door thresholds and at diagonal sawcuts. | 13770.18 | N/A | 13770.18
9 | Fairview 1 | N/A | Site Infrastructure | Urgent (1 Year) | Replace Concrete Pavement - North (Rear) | Two 15'x15' slabs adjacent to the asphalt pavement in front of the 1970 structure are cracked and damaged. | 7254.6 | N/A | 7254.6
10 | Fairview 2 | N/A | Mechanical System | Urgent (1 Year) | Toilet Exhaust Fan - Mens Bath 2 Renewal | Auto generated renewal for Toilet Exhaust Fan - Mens Bath 2. System Description: Est. 150 CFM. | 236 | N/A | 236
11 | Fairview 2 | N/A | Mechanical System | Urgent (1 Year) | Toilet Exhaust Fan - Womens Bath 1 Renewal | Auto generated renewal for Toilet Exhaust Fan - Womens Bath 1. System Description: Est. 150 CFM. | 236 | N/A | 236
12 | Garner 1 | 44.75% | Architectural Systems | Urgent (1 Year) | Code Violation - No Protection Above Ceiling At Sleeping Quarters | Walls separating sleeping rooms from corridor, bathrooms, mechanical, and storage rooms on second floor do not extend above ceiling level, Ceilings are ACT and provide no membrane fire protection. Wood frame attic above is open across entire space and is unprotected. | 10000 | 4475 | 4475
13 | Garner 2 | 44.75% | Site Infrastructure | Urgent (1 Year) | Fencing - Wood - North | Fencing - Wood - North Maintenance | 2286 | 1023.08 | 1023.08
14 | Garner 2 | 44.75% | Site Infrastructure | Urgent (1 Year) | Fencing - Wood - Garage | Fencing - Wood - Garage Maintenance | 457 | 204.49 | 204.49
15 | Garner 3 | 44.75% | Plumbing System | Urgent (1 Year) | Repair Tile Shower Basin | To ensure published lifetime, the damaged tile in the basin of the shower should be replaced. | 987 | 441.76 | 441.76
16 | Garner 3 | 44.75% | Mechanical System | Urgent (1 Year) | DX Split System 1 Renewal | Auto generated renewal for DX Split System 1. System Description: Outdoor condensing unit: 2.5 Tons. Model # 38CKC030500; Serial # 0499E06854. Cooling Coil : 2.5 Tons. Model # 3498XA04200ABAA; Serial # 3498X12247. Gas-Fired Furnace: est. 1000 CFM. Model No. Weathermaker 9200. | 8164 | 3653.6 | 3653.6
17 | Garner 3 | 44.75% | Mechanical System | Urgent (1 Year) | DX Split System 3 Renewal | Auto generated renewal for DX Split System 3. System Description: Outdoor condensing unit: 5 Tons. Model # 38BRC060530; Serial # 0399E02249. Cooling Coil : 5 Tons. Gas-Fired Furnace: est. 2000 CFM. Model No. Weathermaker 9200. | 12571 | 5625.74 | 5625.74
18 | Hopkins | N/A | Mechanical System | Urgent (1 Year) | DX Split System 1 - Living Area Renewal | Auto generated renewal for DX Split System 1 - Living Area. System Description: Outdoor condensing unit: 3 Tons. Model # 2TTR2036A100AA; Serial # 3364TN73F. Cooling Coil: 3 Tons. Gas-Fired Furnace: est. 1000 CFM. (Equipment tag inaccessible.) | 8710 | N/A | 8710
19 | Hopkins | N/A | Architectural | Urgent (1 Year) | Investigate and Repair Leak at Roof/Wall Junction | Water is leaking into building at inside corner intersection of exterior walls of Vehicle bay 06 and Vehicle Bay 07 on South face of building. Leak appear to originate at the top of the wall, possibly from defective gutter termination. | 1085 | N/A | 1085
20 | Hopkins | N/A | Site Infrastructure | Urgent (1 Year) | Replace Asphalt Pavement - Northeast Corner of Building | Replace Asphalt Pavement - Northeast Corner of Building | 2421 | N/A | 2421
21 | Knightdale 1 | 51.28% | Architectural Aesthetics | Urgent (1 Year) | Code Violation: No Fire Wall Between Apparatus Bay and Other Areas | CMU wall separating apparatus bay from admin, dayroom and sleeping quarters area stops at ceiling. Wood frame attic is open above. Fire and Carbon Monoxide risks are increased by absence of appropriate fire separation. | 10000 | 5128 | 5128
22 | Knightdale 1 | 51.28% | Architectural Aesthetics | Urgent (1 Year) | Code Violation: Unfinished Spaces Not Suitable for Occupancy | Storage rooms 18 and 19 have unprotected exposed kraft-faced batt insulation in ceilings and areas of exposed combustible rigid insulation on walls. | 5000 | 2564 | 2564
23 | Knightdale 1 | 51.28% | Site Infrastructure | Urgent (1 Year) | Re-Stripe Accessible Parking and Add Signage | Re-Stripe Accessible Parking and Add Signage | 616 | 315.88 | 315.88
24 | Knightdale 1 | 51.28% | Plumbing System | Urgent (1 Year) | Cross Connection at Soap Dispensing Station Violates Municipal Code | Soap dispensing system used for truck washing is directly connected to hose bib without any backflow prevention. (Majestic Solutions System) A 3/4" backflow preventer should be installed. | 960 | 492.29 | 492.29
25 | Northern Wake 3 | N/A | Electrical System | Urgent (1 Year) | Secure Light Fixture and Meter Base to Brick Veneer | Secure Light Fixture and Meter Base to Brick Veneer | 311 | N/A | 311
26 | Northern Wake 3 | N/A | Architectural Aesthetics | Urgent (1 Year) | Seamless Floor System Failure in Equipment Bay | Seamless floor finish at the northwest corner of Equipment Room 102 is failing under constant exposure to water from nearby interior hose bib. Repair damaged area. | 4272 | N/A | 4272
27 | Northern Wake 4 | N/A | Electrical System | Urgent (1 Year) | Add Exterior Emergency Egress Lighting at Front Door | Add Exterior Emergency Egress Lighting at Front Door | 9410 | N/A | 9410
28 | Swift Creek | N/A | Electrical System | Urgent (1 Year) | Add Code Compliant Emergency and Exit Lighting to Vehicle Bay | Currently only 4 exit lights exist on site with no emergency egress lighting. Recommend bringing facility up to code standards and replacing the existing fixtures at that time. | 13262.4 | N/A | 13262.4
29 | Wake Forest 5 | 23.18% | Architectural Aesthetics | Urgent (1 Year) | Add Accessible Egress at Southeast Exterior Door | Secondary door (southeast exit) does not offer ADA compliant egress. Loose gravel is not compliant and pavers are insufficient. | 1616 | 374.68 | 374.68
30 | Wake Forest 5 | 23.18% | Site Infrastructure | Urgent (1 Year) | Site Development - Wood Deck - Treated Renewal | Auto generated renewal for Site Development - Wood Deck - Treated. System Description: Wood deck including pressure-treated framing, decking, posts, railings, and stairs. | 1862 | 431.7 | 431.7
31 | Wake New Hope 2 | N/A | Building Envelope | Urgent (1 Year) | Repoint Crack in North and South Vehicle Bay Walls | Large stair step crack at east end of north bay wall. Hairline crack at door into living areas on south bay wall. | 1838 | N/A | 1838
32 | Wendell 1 | N/A | Plumbing System | Urgent (1 Year) | Investigate Shower Drainage Issues in Dorm Bathroom | Current chief reported shower drains in both dorm bathrooms were not draining properly causing backup into building. Recommend investigation by plumbing professional to determine cause and/or solution. | 2000 | N/A | 2000
33 | Wendell 2 | N/A | Electrical System | Urgent (1 Year) | Add Monitoring to Fire Alarm Panel | The existing fire alarm system is not monitored. Add (2) phone lines to panel for monitoring. | 1356 | N/A | 1356
34 | Wendell 2 | N/A | Site Infrastructure | Urgent (1 Year) | EMS - Repair Cracks, Seal Coat, and Restripe Existing Parking Lot | Recommend repairing cracks and seal coating the existing surface to prolong lifetime of parking area. | 3458 | N/A | 3458
35 | Wendell 2 | N/A | Site Infrastructure | Urgent (1 Year) | Fire Station - Repair Cracks, Seal Coat, and Restripe Existing Parking Lot | Recommend repairing cracks and seal coating the existing surface to prolong lifetime of parking area. | 3763 | N/A | 3763
36 | Western Wake 1 | N/A | Site Infrastructure | Urgent (1 Year) | Repair Paving Failure at South Rear Entry | Repair Paving Failure at South Rear Entry | 1452 | N/A | 1452
37 | Western Wake 1 | N/A | Site Infrastructure | Urgent (1 Year) | Replace 5 Sections of Concrete Sidewalk at South Door | Replace 5 Sections of Concrete Sidewalk at South Door for Accessibility | 2042 | N/A | 2042
38 | Garner 2 | 44.75% | Plumbing System | Urgent (2-3 Years) | Tile Shower Renewal | Auto generated renewal for Tile Shower. System Description: N/A | 3746.628 | 1676.616 | 1676.616
39 | Hopkins | N/A | Electrical System | Urgent (2-3 Years) | Exterior Linear Lighting Fixtures Renewal | Auto generated renewal for Exterior Linear Lighting Fixtures. System Description: Fluorescent linear lights are located at front entry and east and west elevations (walls). Pricing includes fixtures, wiring, and controls. | 8654 | N/A | 8654
40 | Rolesville | 46.29% | Site Infrastructure | Urgent (2-3 Years) | Re-Stripe and Add Accessible Handicap Space | Install Accessible HC Parking with signage near residence. Install new accessible parking plus accessible route from parking space. | 1210.8 | 560.48 | 560.48
41 | Northern Wake 4 | N/A | Architectural Aesthetics | Urgent (2-3 Years) | Replace Front Storefront System Door | Front door has been repaired and retrofitted with non-standard hardware. Recommended for replacement. | 3120 | N/A | 3120
[8 empty] | TOTAL | 179999.9754
| Fire Department | TOTAL |  |  | Department Type | TOTAL
| 282 Durham Highway Station #1 | 49894.02 |  |  | Non-Profit | 145511.2
| 162 Fairview Fire Station #1 | 21024.78 |  |  | Cost Share | 34488.7754
| 249 Fairview Station #2 | 472
| 262 Garner Station #1 | 5481.875
| 248 Garner Station #2 | 2904.186
| 295 Garner Station #3 | 9721.1
| 273 Hopkins Station #1 | 20870
| 214 Eastern Wake Station #2 Hester St | 8588.8844
| 281 Northern Wake Station # 3 | 9013
| 280 Northern Wake Station # 4 | 15066
| 163 Rolesville Station #1 | 560.48
| 290 Swift Creek Station #1 | 13262.4
| 278 Wake Forest Station #5 | 7232.25
| 275 Wake New Hope Station #2 | 1838
| 271 Wendell Station #1 | 2000
| 274 Wendell Station #2 | 8577
| 164 Western Wake Station #1 | 3494
| TOTAL | 179999.9754

## Staff Recomendation FY24
# | Deficiency Information | [5 empty] | Full Deficiency Cost Estimate
[7 empty] | Total Estimated Cost for FY24 (20% Increase) | Total Cost w/ Cost Share for FY24 | Recommeneded for FY24 Budget
| Station | Cost Share | Type | Priority | Name | Description
1 | Durham Hwy 1 | N/A | Plumbing System | Urgent (2-3 Years) | Mens Restroom Fixtures Renewal | Auto generated renewal for Mens Restroom Fixtures. System Description: Includes 1 vitreous china urinal, 2 water closets, 2 vitreous china wall mounted lavatories and 1 tile shower. | 11168.02 | N/A | 11168.02
2 | Durham Hwy 1 | N/A | Plumbing System | Urgent (2-3 Years) | Womens Restroom Fixtures Renewal | Auto generated renewal for Womens Restroom Fixtures. System Description: Includes 2 water closets, 2 vitreous china wall mounted lavatories and 1 tile shower. | 8244.48 | N/A | 8244.48
3 | Durham Hwy 1 | N/A | Mechanical System | Urgent (2-3 Years) | DX Split System 5 - Floor 2 Renewal | Auto generated renewal for DX Split System 5 - Floor 2. System Description: Outdoor condensing unit: 5 Tons. Model # 2TTA0060A300DAA; Serial # 71947KC3F. Cooling Coil : 5 Tons. Model # 2TXCC060BC3HCAA; Serial # 7102F8A5G. Gas-Fired Furnace: est. 2000 CFM. Model No. XR80. Valuation of system is based on furnace, outside condensing unit, and the cooling coil; pricing does not include ductwork. | 14456.32 | N/A | 14456.32
4 | Garner 1 | 44.75% | Mechanical System | Urgent (2-3 Years) | DX Split System 2 Renewal | Auto generated renewal for DX Split System 2. System Description: Outdoor condensing unit: 7.5 Tons. Goodman unit installed in 2007. Model # GSC10090SAB; Serial # 0704674634. Cooling Coil : 7.5 Tons. 2 Carrier Gas-Fired Furnaces serve the system: est. 1500 CFM each. Valuation of system is based on furnace, outside condensing unit, and the cooling coil; pricing does not include ductwork. | 20788 | 9302.45 | 9302.45
5 | Garner 1 | 44.75% | Mechanical System | Urgent (2-3 Years) | DX Split System 3 Renewal | Auto generated renewal for DX Split System 3. System Description: Outdoor condensing unit: 4 Tons. Goodman unit installed in 2007. Model # GSC130483AF; Serial # 0707599677. Cooling Coil : 4 Tons. Gas-Fired Furnace: est. 1600 CFM. York unit installed 1995. Model # P2MPD020N11201D. Serial # EADM020407. Valuation of system is based on furnace, outside condensing unit, and the cooling coil; pricing does not include ductwork. | 10959 | 4903.99 | 4903.99
6 | Garner 1 | 44.75% | Mechanical System | Urgent (2-3 Years) | DX Split System 4 Renewal | Auto generated renewal for DX Split System 4. System Description: Outdoor condensing unit: 4 Tons. Goodman unit installed in 2007. Cooling only. Model # CK49-1; Serial # 0106491514. Cooling Coil : 4 Tons. Air Handler likely predates 2007 outdoor unit install date. Valuation of system is based on outside condensing unit, air handler, and the cooling coil; pricing does not include ductwork. | 10959 | 4903.99 | 4903.99
7 | Garner 2 | 44.75% | Site Infrastructure | Urgent (2-3 Years) | Re-Stripe Parking Lot After Re-Paving | Re-Stripe Parking Lot After Re-Paving | 458 | 205.1 | 205.1
8 | Garner 2 | 44.75% | Site Infrastructure | Urgent (2-3 Years) | Asphalt Parking Lot - Typical Fire Station Renewal | Auto generated renewal for Asphalt Parking Lot - Typical Fire Station. System Description: N/A | 78132.72 | 34964.3922 | 34964.3922
9 | Garner 3 | 44.75% | Site Infrastructure | Urgent (2-3 Years) | Re-Stripe Parking Lot | Re-Stripe Parking Lot | 1344 | 601.35 | 601.35
10 | Hopkins | N/A | Mechanical System | Urgent (2-3 Years) | DX Split System 3- Sleeping Quarters Renewal | Auto generated renewal for DX Split System 3- Sleeping Quarters. System Description: Outdoor condensing unit: 1.5 Tons. Model # TTB018C100A2; Serial # 4102N7Y5F. Cooling Coil: 1.5 Tons. Gas-Fired Furnace: est. 450 CFM. (Equipment tag was not found.) | 6707 | N/A | 6707
11 | Knightdale 1 | 51.28% | Site Infrastructure | Urgent (2-3 Years) | Add Black Vinyl Coated Chain Link Fence at Top of Wall | Add Black Vinyl Coated Chain Link Fence at Top of Wall | 815 | 417.93 | 417.93
12 | Knightdale 1 | 51.28% | Architectural Aesthetics | Urgent (2-3 Years) | Investigative Study- Upgrade and Re-purpose Unusable Second Floor | Second floor cannot be occupied because it has no code compliant means of egress. Open wood stair is non-compliant. Space is being used for light storage and is in disrepair. It is the inspector's opinion that the second floor and the associated rooms 17, 18, and 19 on the first floor below are unsightly and represent a fire hazard. | 10000 | 5128 | 5128
13 | Northern Wake 4 | N/A | Site Infrastructure | Urgent (2-3 Years) | Replace Damaged Concrete Pavement | (5) Sections at 120 SF Each | 654 | N/A | 654
14 | Northern Wake 4 | N/A | Electrical System | Urgent (2-3 Years) | Exterior Lighting Fixtures Renewal | Auto generated renewal for Exterior Lighting Fixtures. System Description: Incandescent lights are at exterior doors. Pricing includes fixtures, wiring, and controls. | 1951 | N/A | 1951
15 | Wake New Hope 2 | N/A | Plumbing System | Urgent (2-3 Years) | Install Water Softener Equipment | Occupants formerly had a water softener but disconnected it when it developed leaks. Occupants report multiple water related replacements (i.e. piping, premature water heater replacement, etc.); all of these point to hard water issues on site. | 5234 | N/A | 5234
16 | Wake New Hope 2 | N/A | Plumbing System | Urgent (2-3 Years) | Install Oil Interceptor for Vehicle Bay Drain and Re-route Piping to | Trench drains within the Vehicle Bay discharge currently into drainage ditch on the southwest corner of lot. A new oil interceptor should be installed and the drain should be tied into sanitary sewer. Per discussions with on duty Fire Department Staff, the Vehicle Bay (Room #10) trench drain is not connected to an oil water separator. No manhole covers or other service accesses to an existing oil/water separator were observed on site. | 63202 | N/A | 63202
17 | Western Wake 1 | N/A | Plumbing System | Urgent (2-3 Years) | Mens Restroom Fixtures Renewal | Auto generated renewal for Mens Restroom Fixtures. System Description: Includes 2 water closets, 1 vitreous china wall mounted lavatory, 1 vitreous china urinal, and 1 tile shower. | 7204 | N/A | 7204
18 | Western Wake 1 | N/A | Plumbing System | Urgent (2-3 Years) | Womens Restroom Fixtures Renewal | Auto generated renewal for Womens Restroom Fixtures. System Description: Includes 2 water closets, 2 vitreous china wall mounted lavatories and 1 tile shower. | 8244 | N/A | 8244
[8 empty] | TOTAL | 187492.0222
| Fire Department | TOTAL |  |  | Department Type | TOTAL
| 282 Durham Highway Station #1 | 33868.82 |  |  | Non-Profit | 127064.82
| 162 Fairview Fire Station #1 | N/A |  |  | Cost Share | 60427.2022
| 249 Fairview Station #2 | N/A
| 262 Garner Station #1 | 19110.43
| 248 Garner Station #2 | 35169.4922
| 295 Garner Station #3 | 601.35
| 273 Hopkins Station #1 | 6707
| 214 Eastern Wake Station #2 Hester St | 5545.93
| 281 Northern Wake Station # 3 | N/A
| 280 Northern Wake Station # 4 | 2605
| 163 Rolesville Station #1 | N/A
| 290 Swift Creek Station #1 | N/A
| 278 Wake Forest Station #5 | N/A
| 275 Wake New Hope Station #2 | 68436
| 271 Wendell Station #1 | N/A
| 274 Wendell Station #2 | N/A
| 164 Western Wake Station #1 | 15448
| TOTAL | 187492.0222

## Staff Recomendation FY25
# | Deficiency Information | [5 empty] | Full Deficiency Cost Estimate
[7 empty] | Total Estimated Cost for FY25 (20% Increase) | Total Cost w/ Cost Share for FY25 | Recommeneded for FY25 Budget
| Station | Cost Share | Type | Priority | Name | Description
1 | Durham Hwy 1 | N/A | Mechanical System | Near Term (4-7 Years) | DX Split System 2 - Floor 1 Renewal | Auto generated renewal for DX Split System 2 - Floor 1. System Description: Outdoor condensing unit: 4 Tons. Model # 4TTA3048A3000AA; Serial # 7393P874F. Cooling Coil : 4 Tons. Model # 2TXCC049BC3HCAA; Serial # 7415UBU5G. Gas-Fired Furnace: est. 1600 CFM. Model No. XR80. | 10591.72 | N/A | 10591.72
2 | Garner 1 | 44.75% | Architectural Systems | Near Term (4-7 Years) | Install Alum. Quarry Tile Threshold at Overhead Door | Use of aluminum thresholds as a reinforcement to protect vulnerable edge of quarry tile floor system at bay door openings has been successful in reducing breakage of tile where installed at 4 of 8 doors at this station. Department wants same protection at remaining four doors. | 5086 | 2275.81 | 2275.81
3 | Garner 3 | 44.75% | Plumbing System | Near Term (4-7 Years) | Restroom Fixtures - Original Toilet 1 Renewal | Auto generated renewal for Restroom Fixtures - Toilet 1 - original. System Description: Restroom fixtures include a vitreous china water closet and a vitreous china wall mounted lavatory. | 4548 | 2035.24 | 2035.24
4 | Garner 3 | 44.75% | Plumbing System | Near Term (4-7 Years) | Restroom Fixtures - Original Toilet 2 Renewal | Auto generated renewal for Restroom Fixtures - Toilet 2- original. System Description: Restroom fixtures include a vitreous china water closet and a vitreous china wall mounted lavatory. | 1548 | 2035.24 | 2035.24
5 | Hopkins | N/A | Architectural | Near Term (4-7 Years) | Gutters Rusting | Existing Gutters have surface rust forming under and through existing paint coating on the south face of building. | 2500 | N/A | 2500
6 | Northern Wake 3 | N/A | Building Envelope | Near Term (4-7 Years) | Scrape and Paint Steel Lintels | Embedded edge angles at roll-up doors on north side of vehicle bay are corroded. In some areas corrosion is advanced. Angles need to be scraped and painted with cold galvanizing paint in order to prolong their life. | 805 | N/A | 805
7 | Northern Wake 3 | N/A | Architectural Aesthetics | Near Term (4-7 Years) | Re-Caulk Exterior Windows and Doors | Exterior windows and doors need to be recaulked | 2563 | N/A | 2563
8 | Northern Wake 4 | N/A | Architectural Aesthetics | Near Term (4-7 Years) | Install New Roof System Over Existing | Install New Roof System Over Existing | 55964 | N/A | 55964
9 | Northern Wake 4 | N/A | Mechanical Systems | Near Term (4-7 Years) | Apparatus Bay Unit Heater - Gas Fired Renewal | Auto generated renewal for Vehicle Bay Unit Heaters - Gas Fired. System Description: Heating for the apparatus bay is provided by a suspended unit heater, capacity of 75,000 BTUH. | 4897 | N/A | 4897
10 | Wendell 2 | N/A | Mechanical System | Near Term (4-7 Years) | DX Split System 2 - Addition Renewal | Auto generated renewal for DX Split System 2 - Addition. System Description: Outdoor condensing unit: 3.5 Tons. Model # 4TTR4042A10000AA; Serial # 7211M7L2F. Cooling Coil: 3.5 Tons. Model # 4TXCB042BC3HCAA; Serial # 7235BY8SG. Gas-Fired Furnace: est. 1400 CFM. Model No. XR90. | 9542 | N/A | 9542
11 | Wendell 2 | N/A | Mechanical System | Near Term (4-7 Years) | EMS Vehicle Bay Unit Heater- Gas Fired Renewal | Auto generated renewal for Vehicle Bay Unit Heaters - Gas Fired. Heating for the vehicle bay is provided by a suspended unit heater, capacity of 100,000 BTUH. | 3738 | N/A | 3738
12 | Wendell 2 | N/A | Architectural | Near Term (4-7 Years) | Install Fluid Applied Roof Coating | 29 y.o. economy PEMB metal roof system on building is exhibiting signs of fastener neoprene washer failure. Also reported issues of leaks at new/old roof intersection. Recommend installation of fluid applied roof coating to extend the life of original roof area. | 51550 | N/A | 51550
13 | Western Wake 1 | N/A | Architectural Aesthetics | Near Term (4-7 Years) | Re-caulk Masonry Expansion Joints | Masonry expansion joint material is brittle and cracking. | 3797 | N/A | 3797
[8 empty] | TOTAL | 152294.01
| Fire Department | TOTAL |  |  | Department Type | TOTAL
| 282 Durham Highway Station #1 | 10591.72 |  |  | Non-Profit | 145947.72
| 162 Fairview Fire Station #1 | N/A |  |  | Cost Share | 6346.29
| 249 Fairview Station #2 | N/A
| 262 Garner Station #1 | 2275.81
| 248 Garner Station #2 | N/A
| 295 Garner Station #3 | 4070.48
| 273 Hopkins Station #1 | 2500
| 214 Eastern Wake Station #2 Hester St | N/A
| 281 Northern Wake Station # 3 | 3368
| 280 Northern Wake Station # 4 | 60861
| 163 Rolesville Station #1 | N/A
| 290 Swift Creek Station #1 | N/A
| 278 Wake Forest Station #5 | N/A
| 275 Wake New Hope Station #2 | N/A
| 271 Wendell Station #1 | N/A
| 274 Wendell Station #2 | 64830
| 164 Western Wake Station #1 | 3797
| TOTAL | 152294.01

## Staff Recomendation FY26
# | Deficiency Information | [5 empty] | Full Deficiency Cost Estimate
[7 empty] | Total Estimated Cost for FY26 (20% Increase) | Total Cost w/ Cost Share for FY26 | Recommeneded for FY26 Budget
| Station | Cost Share | Type | Priority | Name | Description
1 | Durham Hwy 1 | N/A | Site Infrastructure | Near Term (4-7 Years) | Repair Cracks, Seal Coat, and Restripe Existing Parking Lot | Recommend repairing cracks and seal coating the existing surface to prolong lifetime of parking area. | 14238 | N/A | 14238
2 | Fairview 1 | N/A | Site Infrastructure | Near Term (4-7 Years) | Repair Cracks, Seal Coat, and Restripe Existing Parking Lot | Recommend repairing cracks and seal coating the existing surface to prolong lifetime of parking area. | 10170 | N/A | 10170
3 | Hopkins | N/A | Site Infrastructure | Near Term (4-7 Years) | Repair Cracks and Reseal Access Road | Access road from Fowler Road to rear of station is showing use and can be renewed with a crack repair and reseal of the asphalt. | 5262 | N/A | 5262
4 | Hopkins | N/A | Site Infrastructure | Near Term (4-7 Years) | Partial (NE Parking) - Repair Cracks, Seal Coat, and Restripe Existing Parking Lot | Recommend repairing cracks and seal coating the existing surface to prolong lifetime of parking area. | 848 | N/A | 848
5 | Hopkins | N/A | Site Infrastructure | Near Term (4-7 Years) | Access Road - Repair Cracks, Seal Coat, and Restripe Existing Parking Lot | Recommend repairing cracks and seal coating the existing surface to prolong lifetime of parking area. | 3390 | N/A | 3390
6 | Northern Wake 3 | N/A | Site Infrastructure | Near Term (4-7 Years) | Repair Cracks, Seal Coat, and Restripe Existing Parking Lot | Recommend repairing cracks and seal coating the existing surface to prolong lifetime of parking area. | 7458 | N/A | 7458
7 | Northern Wake 4 | N/A | Site Infrastructure | Near Term (4-7 Years) | Re-Stripe Parking Lot | Re-Stripe Parking Lot | 7541 | N/A | 7541
8 | Rolesville | 46.29% | Site Infrastructure | Near Term (4-7 Years) | Asphalt Parking Lot - Typical Fire Station Renewal | Auto generated renewal for Asphalt Parking Lot - Typical Fire Station. System Description: N/A | 71161.2 | 32940.52 | 32940.52
9 | Wendell 2 | N/A | Site Infrastructure | Near Term (4-7 Years) | Fire Station - Asphalt Parking Lot - Typical Fire Station Renewal | Auto generated renewal for Fire Station - Asphalt Parking Lot - Typical Fire Station. | 20171 | N/A | 20171
10 | Western Wake 1 | N/A | Site Infrastructure | Near Term (4-7 Years) | Repair Cracks, Seal Coat, and Restripe Existing Parking Lot | Recommend repairing cracks and seal coating the existing surface to prolong lifetime of parking area. | 14916 | N/A | 14916
[8 empty] | TOTAL | 116934.52
| Fire Department | TOTAL |  |  | Department Type | TOTAL
| 282 Durham Highway Station #1 | 14238 |  |  | Non-Profit | 83994
| 162 Fairview Fire Station #1 | 10170 |  |  | Cost Share | 32940.52
| 249 Fairview Station #2 | N/A
| 262 Garner Station #1 | N/A
| 248 Garner Station #2 | N/A
| 295 Garner Station #3 | N/A
| 273 Hopkins Station #1 | 9500
| 214 Eastern Wake Station #2 Hester St | N/A
| 281 Northern Wake Station # 3 | 7458
| 280 Northern Wake Station # 4 | 7541
| 163 Rolesville Station #1 | 32940.52
| 290 Swift Creek Station #1 | N/A
| 278 Wake Forest Station #5 | N/A
| 275 Wake New Hope Station #2 | N/A
| 271 Wendell Station #1 | N/A
| 274 Wendell Station #2 | 20171
| 164 Western Wake Station #1 | 14916
| TOTAL | 116934.52

## Durham Highway 1
FACILITY CONDITION ASSESSMENTS
282 Durham Highway Station #1
# | Deficiency Information |  |  |  |  | Full Deficiency Cost Estimate
[6 empty] | Estimate | Permit & Fees | Owner Contingency | TOTAL COST | TOTAL COST (20% Increase)
| Type | Priority |  | Name | Description |  | 3% | 10% | (2017 $) | (2021 $)
1 | Architectural Aesthetics | 1 | Urgent (1 Year) | Add Second means of Egress from Second Floor | Nine beds and a 1900 SF dayroom exist on the 2352 FS second floor. Code at time of construction allowed a single exit for Group B if less than 3500 sf and serving fewer than 40 person, and for R-1 with fewer than 4 dwelling units. Current Code required 2 exists if second floor occupant load is greater than 10. At 100 sf/person for Group B area plus none beds equals a current occupant load of 27. Although not mandatory a second exist is recommended to improve life safety. | 36795 | 1103.85 | 3679.5 | 41578.35 | 49894.02
2 | Plumbing System | 3 | Urgent (2-3 Years) | Mens Restroom Fixtures Renewal | Auto generated renewal for Mens Restroom Fixtures. System Description: Includes 1 vitreous china urinal, 2 water closets, 2 vitreous china wall mounted lavatories and 1 tile shower. | 8236 | 247.08 | 823.6 | 9306.68 | 11168.016
3 | Plumbing System | 3 | Urgent (2-3 Years) | Womens Restroom Fixtures Renewal | Auto generated renewal for Womens Restroom Fixtures. System Description: Includes 2 water closets, 2 vitreous china wall mounted lavatories and 1 tile shower. | 6080 | 182.4 | 608 | 6870.4 | 8244.48
4 | Mechanical System | 3 | Urgent (2-3 Years) | DX Split System 5 - Floor 2 Renewal | Auto generated renewal for DX Split System 5 - Floor 2. System Description: Outdoor condensing unit: 5 Tons. Model # 2TTA0060A300DAA; Serial # 71947KC3F. Cooling Coil : 5 Tons. Model # 2TXCC060BC3HCAA; Serial # 7102F8A5G. Gas-Fired Furnace: est. 2000 CFM. Model No. XR80. Valuation of system is based on furnace, outside condensing unit, and the cooling coil; pricing does not include ductwork. | 10661 | 319.83 | 1066.1 | 12046.93 | 14456.316
5 | Mechanical System | 5 | Near Term (4-7 Years) | DX Split System 2 - Floor 1 Renewal | Auto generated renewal for DX Split System 2 - Floor 1. System Description: Outdoor condensing unit: 4 Tons. Model # 4TTA3048A3000AA; Serial # 7393P874F. Cooling Coil : 4 Tons. Model # 2TXCC049BC3HCAA; Serial # 7415UBU5G. Gas-Fired Furnace: est. 1600 CFM. Model No. XR80. | 7811 | 234.33 | 781.1 | 8826.43 | 10591.716
6 | Site Infrastructure | 5 | Near Term (4-7 Years) | Repair Cracks, Seal Coat, and Restripe Existing Parking Lot | Recommend repairing cracks and seal coating the existing surface to prolong lifetime of parking area. | 10500 | 315 | 1050 | 11865 | 14238
[9 empty] | Urgent (Immediate) | 0
[9 empty] | Urgent (1 Year) | 49894.02
[9 empty] | Urgent (2-3 Years) | 33868.812
[9 empty] | Near Term (4-7 Years) | 24829.716
[9 empty] | GRAND TOTALS | 108592.548

## Fairview 1
FACILITY CONDITION ASSESSMENTS
162 Fairview Fire Station #1
# | Deficiency Information |  |  |  |  | Full Deficiency Cost Estimate
[6 empty] | Estimate | Permit & Fees | Owner Contingency | TOTAL COST | TOTAL COST (20% Increase)
| Type | Priority |  | Name | Description |  | 3% | 10% | (2017 $) | (2021 $)
1 | Architectural Aesthetics | 1 | Urgent (1 Year) | Repair Quarry Tile Floor in Apparatus Bay | Quarry Tile system in apparatus bay 101 isexhibiting areas of breakage and loosening of tiles. Particular weak points were observed at overhead door thresholds and at diagonal sawcuts. | 10155 | 304.65 | 1015.5 | 11475.15 | 13770.18
2 | Site Infrastructure | 1 | Urgent (1 Year) | Replace Concrete Pavement - North (Rear) | Two 15'x15' slabs adjacent to the asphalt pavement in front of the 1970 structure are cracked and damaged. | 5350 | 160.5 | 535 | 6045.5 | 7254.6
3 | Site Infrastructure | 5 | Near Term (4-7 Years) | Repair Cracks, Seal Coat, and Restripe Existing Parking Lot | Recommend repairing cracks and seal coating the existing surface to prolong lifetime of parking area. | 7500 | 225 | 750 | 8475 | 10170
[9 empty] | Urgent (Immediate) | 0
[9 empty] | Urgent (1 Year) | 21024.78
[9 empty] | Urgent (2-3 Years) | 0
[9 empty] | Near Term (4-7 Years) | 10170
[9 empty] | GRAND TOTALS | 31194.78

## Fairview 2
FACILITY CONDITION ASSESSMENTS
249 Fairview Station #2
# | Deficiency Information |  |  |  |  | Full Deficiency Cost Estimate
[6 empty] | Estimate | Permit & Fees | Owner Contingency | TOTAL COST | TOTAL COST (20% Increase)
| Type | Priority |  | Name | Description |  | 3% | 10% | (2017 $) | (2021 $)
1 | Mechanical System | 1 | Urgent (1 Year) | Toilet Exhaust Fan - Mens Bath 2 Renewal | Auto generated renewal for Toilet Exhaust Fan - Mens Bath 2. System Description: Est. 150 CFM. | 174 | 5.22 | 17.4 | 196.62 | 236
2 | Mechanical System | 1 | Urgent (1 Year) | Toilet Exhaust Fan - Womens Bath 1 Renewal | Auto generated renewal for Toilet Exhaust Fan - Womens Bath 1. System Description: Est. 150 CFM. | 174 | 5.22 | 17.4 | 196.62 | 236
[9 empty] | Urgent (Immediate) | 0
[9 empty] | Urgent (1 Year) | 472
[9 empty] | Urgent (2-3 Years) | 0
[9 empty] | Near Term (4-7 Years) | 0
[9 empty] | GRAND TOTALS | 472

## Garner 1
FACILITY CONDITION ASSESSMENTS
262 Garner Station #1
# | Deficiency Information |  |  |  |  | Full Deficiency Cost Estimate
[6 empty] | Estimate | Permit & Fees | Owner Contingency | TOTAL COST | TOTAL COST (20% Increase) | Cost Share Amount
| Type | Priority |  | Name | Description |  | 3% | 10% | (2017 $) | (2021 $) | 44.75%
1 | Mechanical System | 0 | Urgent (Immediate) | Replace Indoor AHU Component for DX Split System 4 | Indoor air handler was observed to be in poor/unreliable condition at assessment inspection. Recommend immediate replacement of this component only due to poor life expectancy. | 1659 | 50 | 165.9 | 1875 | 2250 | 1006.875
2 | Architectural Systems | 1 | Urgent (1 Year) | Code Violation - No Protection Above Ceiling At Sleeping Quarters | Walls separating sleeping rooms from corridor, bathrooms, mechanical, and storage rooms on second floor do not extend above ceiling level, Ceilings are ACT and provide no membrane fire protection. Wood frame attic above is open across entire space and is unprotected. | 0 | 0 | 0 | 0 | 10000 | 4475
3 | Mechanical System | 3 | Urgent (2-3 Years) | DX Split System 2 Renewal | Auto generated renewal for DX Split System 2. System Description: Outdoor condensing unit: 7.5 Tons. Goodman unit installed in 2007. Model # GSC10090SAB; Serial # 0704674634. Cooling Coil : 7.5 Tons. 2 Carrier Gas-Fired Furnaces serve the system: est. 1500 CFM each. Valuation of system is based on furnace, outside condensing unit, and the cooling coil; pricing does not include ductwork. | 15330 | 460 | 1533 | 17323 | 20787.6 | 9302.451
4 | Mechanical System | 3 | Urgent (2-3 Years) | DX Split System 3 Renewal | Auto generated renewal for DX Split System 3. System Description: Outdoor condensing unit: 4 Tons. Goodman unit installed in 2007. Model # GSC130483AF; Serial # 0707599677. Cooling Coil : 4 Tons. Gas-Fired Furnace: est. 1600 CFM. York unit installed 1995. Model # P2MPD020N11201D. Serial # EADM020407. Valuation of system is based on furnace, outside condensing unit, and the cooling coil; pricing does not include ductwork. | 8082 | 242 | 808.2 | 9132.2 | 10958.64 | 4903.9914
5 | Mechanical System | 3 | Urgent (2-3 Years) | DX Split System 4 Renewal | Auto generated renewal for DX Split System 4. System Description: Outdoor condensing unit: 4 Tons. Goodman unit installed in 2007. Cooling only. Model # CK49-1; Serial # 0106491514. Cooling Coil : 4 Tons. Air Handler likely predates 2007 outdoor unit install date. Valuation of system is based on outside condensing unit, air handler, and the cooling coil; pricing does not include ductwork. | 8082 | 242 | 808.2 | 9132.2 | 10958.64 | 4903.9914
6 | Architectural Systems | 5 | Near Term (4-7 Years) | Install Alum. Quarry Tile Threshold at Overhead Door | Use of aluminum thresholds as a reinforcement to protect vulnerable edge of quarry tile floor system at bay door openings has been successful in reducing breakage of tile where installed at 4 of 8 doors at this station. Department wants same protection at remaining four doors. | 3750 | 113 | 375 | 4238 | 5085.6 | 2275.806
[9 empty] | Urgent (Immediate) | 2250 | 1006.875
[9 empty] | Urgent (1 Year) | 10000 | 4475
[9 empty] | Urgent (2-3 Years) | 42704.88 | 19110.4338
[9 empty] | Near Term (4-7 Years) | 5085.6 | 2275.806
[10 empty] | Total w/o Cost Share | Cost Share Total
[9 empty] | GRAND TOTALS | 60040.48 | 26868.1148

## Garner 2
FACILITY CONDITION ASSESSMENTS
248 Garner Station #2
# | Deficiency Information |  |  |  |  | Full Deficiency Cost Estimate
[6 empty] | Estimate | Permit & Fees | Owner Contingency | TOTAL COST | TOTAL COST (20% Increase) | Cost Share Amount
| Type | Priority |  | Name | Description |  | 3% | 10% | (2017 $) | (2021 $) | 44.75%
1 | Site Infrastructure | 1 | Urgent (1 Year) | Fencing - Wood - North | Fencing - Wood - North Maintenance | 1686 | 50.58 | 168.6 | 1905.18 | 2286.216 | 1023.0817
2 | Site Infrastructure | 1 | Urgent (1 Year) | Fencing - Wood - Garage | Fencing - Wood - Garage Maintenance | 337 | 10.11 | 33.7 | 380.81 | 456.972 | 204.495
3 | Site Infrastructure | 3 | Urgent (2-3 Years) | Re-Stripe Parking Lot After Re-Paving | Re-Stripe Parking Lot After Re-Paving | 338 | 10.14 | 33.8 | 381.94 | 458.328 | 205.1018
4 | Site Infrastructure | 3 | Urgent (2-3 Years) | Asphalt Parking Lot - Typical Fire Station Renewal | Auto generated renewal for Asphalt Parking Lot - Typical Fire Station. System Description: N/A | 57620 | 1728.6 | 5762 | 65110.6 | 78132.72 | 34964.3922
5 | Plumbing System | 3 | Urgent (2-3 Years) | Tile Shower Renewal | Auto generated renewal for Tile Shower. System Description: N/A | 2763 | 82.89 | 276.3 | 3122.19 | 3746.628 | 1676.616
[9 empty] | Urgent (Immediate) | 0 | 0
[9 empty] | Urgent (1 Year) | 2743.188 | 1227.5766
[9 empty] | Urgent (2-3 Years) | 82337.676 | 36846.11
[9 empty] | Near Term (4-7 Years) | 0 | 0
[10 empty] | Total w/o Cost Share | Cost Share Total
[9 empty] | GRAND TOTALS | 85080.864 | 38073.6866

## Garner 3
FACILITY CONDITION ASSESSMENTS
295 Garner Station #3
# | Deficiency Information |  |  |  |  | Full Deficiency Cost Estimate
[6 empty] | Estimate | Permit & Fees | Owner Contingency | TOTAL COST | TOTAL COST (20% Increase) | Cost Share Amount
| Type | Priority |  | Name | Description |  | 3% | 10% | (2017 $) | (2021 $) | 44.75%
1 | Plumbing System | 1 | Urgent (1 Year) | Repair Tile Shower Basin | To ensure published lifetime, the damaged tile in the basin of the shower should be replaced. | 728 | 21.84 | 72.8 | 822.64 | 987.168 | 441.7577
2 | Mechanical System | 1 | Urgent (1 Year) | DX Split System 1 Renewal | Auto generated renewal for DX Split System 1. System Description: Outdoor condensing unit: 2.5 Tons. Model # 38CKC030500; Serial # 0499E06854. Cooling Coil : 2.5 Tons. Model # 3498XA04200ABAA; Serial # 3498X12247. Gas-Fired Furnace: est. 1000 CFM. Model No. Weathermaker 9200. | 6021 | 180.63 | 602.1 | 6803.73 | 8164.476 | 3653.603
3 | Mechanical System | 1 | Urgent (1 Year) | DX Split System 3 Renewal | Auto generated renewal for DX Split System 3. System Description: Outdoor condensing unit: 5 Tons. Model # 38BRC060530; Serial # 0399E02249. Cooling Coil : 5 Tons. Gas-Fired Furnace: est. 2000 CFM. Model No. Weathermaker 9200. | 9271 | 278.13 | 927.1 | 10476.23 | 12571.476 | 5625.7355
4 | Site Infrastructure | 3 | Urgent (2-3 Years) | Re-Stripe Parking Lot | Re-Stripe Parking Lot | 991 | 29.73 | 99.1 | 1119.83 | 1343.796 | 601.3487
5 | Plumbing System | 4 | Near Term (4-7 Years) | Restroom Fixtures - Original Toilet 1 Renewal | Auto generated renewal for Restroom Fixtures - Toilet 1 - original. System Description: Restroom fixtures include a vitreous china water closet and a vitreous china wall mounted lavatory. | 3354 | 100.62 | 335.4 | 3790.02 | 4548.024 | 2035.2407
6 | Plumbing System | 4 | Near Term (4-7 Years) | Restroom Fixtures - Original Toilet 2 Renewal | Auto generated renewal for Restroom Fixtures - Toilet 2- original. System Description: Restroom fixtures include a vitreous china water closet and a vitreous china wall mounted lavatory. | 3354 | 100.62 | 335.4 | 3790.02 | 4548.024 | 2035.2407
[9 empty] | Urgent (Immediate) | 0 | 0
[9 empty] | Urgent (1 Year) | 21723.12 | 9721.0962
[9 empty] | Urgent (2-3 Years) | 1343.796 | 601.3487
[9 empty] | Near Term (4-7 Years) | 9096.048 | 4070.4815
[10 empty] | Total w/o Cost Share | Cost Share Total
[9 empty] | GRAND TOTALS | 32162.964 | 14392.9264

## Hopkins
FACILITY CONDITION ASSESSMENTS
273 Hopkins Station #1
# | Deficiency Information |  |  |  |  | Full Deficiency Cost Estimate
[6 empty] | Estimate | Permit & Fees | Owner Contingency | TOTAL COST | TOTAL COST (20% Increase)
| Type | Priority |  | Name | Description |  | 3% | 10% | (2017 $) | (2021 $)
1 | Mechanical System | 1 | Urgent (1 Year) | DX Split System 1 - Living Area Renewal | Auto generated renewal for DX Split System 1 - Living Area. System Description: Outdoor condensing unit: 3 Tons. Model # 2TTR2036A100AA; Serial # 3364TN73F. Cooling Coil: 3 Tons. Gas-Fired Furnace: est. 1000 CFM. (Equipment tag inaccessible.) | 6423 | 192.69 | 642.3 | 7257.99 | 8710
2 | Architectural | 1 | Urgent (1 Year) | Investigate and Repair Leak at Roof/Wall Junction | Water is leaking into building at inside corner intersection of exterior walls of Vehicle bay 06 and Vehicle Bay 07 on South face of building. Leak appear to originate at the top of the wall, possibly from defective gutter termination. | 800 | 24 | 80 | 904 | 1085
3 | Site Infrastructure | 1 | Urgent (1 Year) | Replace Asphalt Pavement - Northeast Corner of Building | Replace Asphalt Pavement - Northeast Corner of Building | 1785 | 53.55 | 178.5 | 2017.05 | 2421
9 | Electrical System | 2 | Urgent (2-3 Years) | Exterior Linear Lighting Fixtures Renewal | Auto generated renewal for Exterior Linear Lighting Fixtures. System Description: Fluorescent linear lights are located at front entry and east and west elevations (walls). Pricing includes fixtures, wiring, and controls. | 6382 | 191.46 | 638.2 | 7211.66 | 8654
4 | Mechanical System | 2 | Urgent (2-3 Years) | DX Split System 3- Sleeping Quarters Renewal | Auto generated renewal for DX Split System 3- Sleeping Quarters. System Description: Outdoor condensing unit: 1.5 Tons. Model # TTB018C100A2; Serial # 4102N7Y5F. Cooling Coil: 1.5 Tons. Gas-Fired Furnace: est. 450 CFM. (Equipment tag was not found.) | 4946 | 148.38 | 494.6 | 5588.98 | 6707
5 | Architectural | 4 | Near Term (4-7 Years) | Gutters Rusting | Existing Gutters have surface rust forming under and through existing paint coating on the south face of building. | 0 | 0 | 0 | 0 | 2500
6 | Site Infrastructure | 5 | Near Term (4-7 Years) | Repair Cracks and Reseal Access Road | Access road from Fowler Road to rear of station is showing use and can be renewed with a crack repair and reseal of the asphalt. | 3880 | 116.4 | 388 | 4384.4 | 5262
7 | Site Infrastructure | 5 | Near Term (4-7 Years) | Partial (NE Parking) - Repair Cracks, Seal Coat, and Restripe Existing Parking Lot | Recommend repairing cracks and seal coating the existing surface to prolong lifetime of parking area. | 625 | 18.75 | 62.5 | 706.25 | 848
8 | Site Infrastructure | 5 | Near Term (4-7 Years) | Access Road - Repair Cracks, Seal Coat, and Restripe Existing Parking Lot | Recommend repairing cracks and seal coating the existing surface to prolong lifetime of parking area. | 2500 | 75 | 250 | 2825 | 3390
[9 empty] | Urgent (Immediate) | 0
[9 empty] | Urgent (1 Year) | 12216
[9 empty] | Urgent (2-3 Years) | 15361
[9 empty] | Near Term (4-7 Years) | 12000
[9 empty] | GRAND TOTALS | 39577

## Knightdale Station 1
FACILITY CONDITION ASSESSMENTS
214 Eastern Wake Station #2 Hester St
# | Deficiency Information |  |  |  |  | Full Deficiency Cost Estimate
[6 empty] | Estimate | Permit & Fees | Owner Contingency | TOTAL COST | TOTAL COST (20% Increase) | Cost Share Amount
| Type | Priority |  | Name | Description |  | 3% | 10% | (2017 $) | (2021 $) | 51.28%
1 | Architectural Aesthetics | 0 | Urgent (Immediate) | Reinforce Center Stair Stringer Lap Connection | Reinforce Center Stair Stringer Lap Connection | 127 | 4 | 13 | 144 | 173 | 88.7144
2 | Architectural Aesthetics | 1 | Urgent (1 Year) | Code Violation: No Fire Wall Between Apparatus Bay and Other Areas | CMU wall separating apparatus bay from admin, dayroom and sleeping quarters area stops at ceiling. Wood frame attic is open above. Fire and Carbon Monoxide risks are increased by absence of appropriate fire separation. | 0 | 0 | 0 | 0 | 10000 | 5128
3 | Architectural Aesthetics | 1 | Urgent (1 Year) | Code Violation: Unfinished Spaces Not Suitable for Occupancy | Storage rooms 18 and 19 have unprotected exposed kraft-faced batt insulation in ceilings and areas of exposed combustible rigid insulation on walls. | 0 | 0 | 0 | 0 | 5000 | 2564
4 | Site Infrastructure | 1 | Urgent (1 Year) | Re-Stripe Accessible Parking and Add Signage | Re-Stripe Accessible Parking and Add Signage | 454 | 14 | 45 | 513 | 616 | 315.8848
5 | Plumbing System | 1 | Urgent (1 Year) | Cross Connection at Soap Dispensing Station Violates Municipal Code | Soap dispensing system used for truck washing is directly connected to hose bib without any backflow prevention. (Majestic Solutions System) A 3/4" backflow preventer should be installed. | 708 | 21 | 71 | 800 | 960 | 492.288
6 | Site Infrastructure | 2 | Urgent (2-3 Years) | Add Black Vinyl Coated Chain Link Fence at Top of Wall | Add Black Vinyl Coated Chain Link Fence at Top of Wall | 600 | 18 | 60 | 678 | 815 | 417.932
7 | Architectural Aesthetics | 2 | Urgent (2-3 Years) | Investigative Study- Upgrade and Re-purpose Unusable Second Floor | Second floor cannot be occupied because it has no code compliant means of egress. Open wood stair is non-compliant. Space is being used for light storage and is in disrepair. It is the inspector's opinion that the second floor and the associated rooms 17, 18, and 19 on the first floor below are unsightly and represent a fire hazard. | 0 | 0 | 0 | 0 | 10000 | 5128
[9 empty] | Urgent (Immediate) | 173 | 88.7144
[9 empty] | Urgent (1 Year) | 16576 | 8500.1728
[9 empty] | Urgent (2-3 Years) | 10815 | 5545.932
[9 empty] | Near Term (4-7 Years) | 0 | 0
[10 empty] | Total w/o Cost Share | Cost Share Total
[9 empty] | GRAND TOTALS | 27564 | 14134.8192

## Northern Wake 3
FACILITY CONDITION ASSESSMENTS
281 Northern Wake Station # 3
# | Deficiency Information |  |  |  |  | Full Deficiency Cost Estimate
[6 empty] | Estimate | Permit & Fees | Owner Contingency | TOTAL COST | TOTAL COST (20% Increase)
| Type | Priority |  | Name | Description |  | 3% | 10% | (2017 $) | (2021 $)
1 | Electrical System | 0 | Urgent (Immediate) | Exterior Lighting Fixtures - Original Renewal | Auto generated renewal for Exterior Lighting Fixtures - Original. System Description: Incandescent lights are at exterior doors. 1 can light in soffit. Pricing includes fixtures, wiring, and controls. | 3267 | 98 | 327 | 3692 | 4430.4
2 | Electrical System | 1 | Urgent (1 Year) | Secure Light Fixture and Meter Base to Brick Veneer | Secure Light Fixture and Meter Base to Brick Veneer | 229 | 7 | 23 | 259 | 310.8
3 | Architectural Aesthetics | 1 | Urgent (1 Year) | Seamless Floor System Failure in Equipment Bay | Seamless floor finish at the northwest corner of Equipment Room 102 is failing under constant exposure to water from nearby interior hose bib. Repair damaged area. | 3150 | 95 | 315 | 3560 | 4272
4 | Building Envelope | 5 | Near Term (4-7 Years) | Scrape and Paint Steel Lintels | Embedded edge angles at roll-up doors on north side of vehicle bay are corroded. In some areas corrosion is advanced. Angles need to be scraped and painted with cold galvanizing paint in order to prolong their life. | 594 | 18 | 59 | 671 | 805.2
5 | Architectural Aesthetics | 5 | Near Term (4-7 Years) | Re-Caulk Exterior Windows and Doors | Exterior windows and doors need to be recaulked | 1890 | 57 | 189 | 2136 | 2563.2
6 | Site Infrastructure | 5 | Near Term (4-7 Years) | Repair Cracks, Seal Coat, and Restripe Existing Parking Lot | Recommend repairing cracks and seal coating the existing surface to prolong lifetime of parking area. | 5500 | 165 | 550 | 6215 | 7458
[9 empty] | Urgent (Immediate) | 4430.4
[9 empty] | Urgent (1 Year) | 4582.8
[9 empty] | Urgent (2-3 Years) | 0
[9 empty] | Near Term (4-7 Years) | 10826.4
[9 empty] | GRAND TOTALS | 19839.6

## Northern Wake 4
FACILITY CONDITION ASSESSMENTS
280 Northern Wake Station # 4
# | Deficiency Information |  |  |  |  | Full Deficiency Cost Estimate
[6 empty] | Estimate | Permit & Fees | Owner Contingency | TOTAL COST | TOTAL COST (20% Increase)
| Type | Priority |  | Name | Description |  | 3% | 10% | (2017 $) | (2021 $)
1 | Electrical System | 0 | Urgent (Immediate) | Bay Lighting - Original HID and Linear Fluorescent Renewal | Auto generated renewal for Bay Lighting - Original HID and Linear Fluorescent. System Description: Pendant Round | 1870 | 56 | 187 | 2113 | 2535.6
2 | Electrical System | 1 | Urgent (1 Year) | Add Exterior Emergency Egress Lighting at Front Door | Add Exterior Emergency Egress Lighting at Front Door | 6940 | 208 | 694 | 7842 | 9410.4
3 | Site Infrastructure | 2 | Urgent (2-3 Years) | Replace Damaged Concrete Pavement | (5) Sections at 120 SF Each | 483 | 14 | 48 | 545 | 654
4 | Electrical System | 2 | Urgent (2-3 Years) | Exterior Lighting Fixtures Renewal | Auto generated renewal for Exterior Lighting Fixtures. System Description: Incandescent lights are at exterior doors. Pricing includes fixtures, wiring, and controls. | 1439 | 43 | 144 | 1626 | 1951.2
5 | Architectural Aesthetics | 2 | Urgent (2-3 Years) | Replace Front Storefront System Door | Front door has been repaired and retrofitted with non-standard hardware. Recommended for replacement. | 2301 | 69 | 230 | 2600 | 3120
6 | Architectural Aesthetics | 5 | Near Term (4-7 Years) | Install New Roof System Over Existing | Install New Roof System Over Existing | 41272 | 1238 | 4127 | 46637 | 55964.4
7 | Mechanical Systems | 5 | Near Term (4-7 Years) | Apparatus Bay Unit Heater - Gas Fired Renewal | Auto generated renewal for Vehicle Bay Unit Heaters - Gas Fired. System Description: Heating for the apparatus bay is provided by a suspended unit heater, capacity of 75,000 BTUH. | 3612 | 108 | 361 | 4081 | 4897.2
8 | Site Infrastructure | 5 | Near Term (4-7 Years) | Re-Stripe Parking Lot | Re-Stripe Parking Lot | 5561 | 167 | 556 | 6284 | 7540.8
[9 empty] | Urgent (Immediate) | 2535.6
[9 empty] | Urgent (1 Year) | 9410.4
[9 empty] | Urgent (2-3 Years) | 5725.2
[9 empty] | Near Term (4-7 Years) | 68402.4
[9 empty] | GRAND TOTALS | 86073.6

## Rolesville
FACILITY CONDITION ASSESSMENTS
163 Rolesville Station #1
# | Deficiency Information |  |  |  |  | Full Deficiency Cost Estimate
[6 empty] | Estimate | Permit & Fees | Owner Contingency | TOTAL COST | TOTAL COST (20% Increase) | Cost Share Amount
| Type | Priority |  | Name | Description |  | 3% | 10% | (2017 $) | (2021 $) | 46.29%
1 | Site Infrastructure | 2 | Urgent (2-3 Years) | Re-Stripe and Add Accessible Handicap Space | Install Accessible HC Parking with signage near residence. Install new accessible parking plus accessible route from parking space. | 893 | 27 | 89 | 1009 | 1210.8 | 560.4793
2 | Site Infrastructure | 5 | Near Term (4-7 Years) | Asphalt Parking Lot - Typical Fire Station Renewal | Auto generated renewal for Asphalt Parking Lot - Typical Fire Station. System Description: N/A | 52479 | 1574 | 5248 | 59301 | 71161.2 | 32940.5195
[9 empty] | Urgent (Immediate) | 0 | 0
[9 empty] | Urgent (1 Year) | 0 | 0
[9 empty] | Urgent (2-3 Years) | 1210.8 | 560.4793
[9 empty] | Near Term (4-7 Years) | 71161.2 | 32940.5195
[10 empty] | Total w/o Cost Share | Cost Share Total
[9 empty] | GRAND TOTALS | 72372 | 33500.9988

## Swift Creek
FACILITY CONDITION ASSESSMENTS
290 Swift Creek Station #1
# | Deficiency Information |  |  |  |  | Full Deficiency Cost Estimate
[6 empty] | Estimate | Permit & Fees | Owner Contingency | TOTAL COST | TOTAL COST (20% Increase)
| Type | Priority |  | Name | Description |  | 3% | 10% | (2017 $) | (2021 $)
1 | Electrical System | 1 | Urgent (1 Year) | Add Code Compliant Emergency and Exit Lighting to Vehicle Bay | Currently only 4 exit lights exist on site with no emergency egress lighting. Recommend bringing facility up to code standards and replacing the existing fixtures at that time. | 9781 | 293 | 978 | 11052 | 13262.4
[9 empty] | Urgent (Immediate) | 0
[9 empty] | Urgent (1 Year) | 13262.4
[9 empty] | Urgent (2-3 Years) | 0
[9 empty] | Near Term (4-7 Years) | 0
[9 empty] | GRAND TOTALS | 13262.4

## Wake Forest 5
FACILITY CONDITION ASSESSMENTS
278 Wake Forest Station #5
# | Deficiency Information |  |  |  |  | Full Deficiency Cost Estimate
[6 empty] | Estimate | Permit & Fees | Owner Contingency | TOTAL COST | TOTAL COST (20% Increase) | Cost Share Amount
| Type | Priority |  | Name | Description |  | 3% | 10% | (2017 $) | (2021 $) | 23.18%
1 | Plumbing System | 0 | Urgent (Immediate) | Shower Discharges to Grade | Shower drain piping runs underground and discharges into ditch at rear of property. The discharge occurs at NE segment of ditch adjacent to the neighbor's property. Shower should be connected to main septic system. | 2007 | 60 | 201 | 2268 | 2721.6 | 630.8669
2 | Plumbing System | 0 | Urgent (Immediate) | Septic System Renewal | Auto generated renewal for Septic System. System Description: System includes tank and leaching field. Septic field is insufficient and requires pumping every 60 days. Pumping this often isn't an efficient use of funds. Chief said septic field was compromised during the construction of Falls of Neuse Road. Recommend tying into municipal sewer. | 0 | 0 | 0 | 0 | 25000 | 5795
3 | Architectural Aesthetics | 1 | Urgent (1 Year) | Add Accessible Egress at Southeast Exterior Door | Secondary door (southeast exit) does not offer ADA compliant egress. Loose gravel is not compliant and pavers are insufficient. | 1192 | 36 | 119 | 1347 | 1616.4 | 374.6815
4 | Site Infrastructure | 1 | Urgent (1 Year) | Site Development - Wood Deck - Treated Renewal | Auto generated renewal for Site Development - Wood Deck - Treated. System Description: Wood deck including pressure-treated framing, decking, posts, railings, and stairs. | 1374 | 41 | 137 | 1552 | 1862.4 | 431.7043
[9 empty] | Urgent (Immediate) | 27721.6 | 6425.8669
[9 empty] | Urgent (1 Year) | 3478.8 | 806.3858
[9 empty] | Urgent (2-3 Years) | 0 | 0
[9 empty] | Near Term (4-7 Years) | 0 | 0
[10 empty] | Total w/o Cost Share | Cost Share Total
[9 empty] | GRAND TOTALS | 31200.4 | 7232.2527

## Wake New Hope 2
FACILITY CONDITION ASSESSMENTS
275 Wake New Hope Station #2
# | Deficiency Information |  |  |  |  | Full Deficiency Cost Estimate
[6 empty] | Estimate | Permit & Fees | Owner Contingency | TOTAL COST | TOTAL COST (20% Increase)
| Type | Priority |  | Name | Description |  | 3% | 10% | (2017 $) | (2021 $)
1 | Building Envelope | 1 | Urgent (1 Year) | Repoint Crack in North and South Vehicle Bay Walls | Large stair step crack at east end of north bay wall. Hairline crack at door into living areas on south bay wall. | 1355 | 41 | 136 | 1532 | 1838.4
2 | Plumbing System | 2 | Urgent (2-3 Years) | Install Water Softener Equipment | Occupants formerly had a water softener but disconnected it when it developed leaks. Occupants report multiple water related replacements (i.e. piping, premature water heater replacement, etc.); all of these point to hard water issues on site. | 3860 | 116 | 386 | 4362 | 5234.4
3 | Plumbing System | 2 | Urgent (2-3 Years) | Install Oil Interceptor for Vehicle Bay Drain and Re-route Piping to | Trench drains within the Vehicle Bay discharge currently into drainage ditch on the southwest corner of lot. A new oil interceptor should be installed and the drain should be tied into sanitary sewer. Per discussions with on duty Fire Department Staff, the Vehicle Bay (Room #10) trench drain is not connected to an oil water separator. No manhole covers or other service accesses to an existing oil/water separator were observed on site. | 47520 | 1188 | 3960 | 52668 | 63201.6
[9 empty] | Urgent (Immediate) | 0
[9 empty] | Urgent (1 Year) | 1838.4
[9 empty] | Urgent (2-3 Years) | 68436
[9 empty] | Near Term (4-7 Years) | 0
[9 empty] | GRAND TOTALS | 70274.4

## Wendell 1
FACILITY CONDITION ASSESSMENTS
271 Wendell Station #1
# | Deficiency Information |  |  |  |  | Full Deficiency Cost Estimate
[6 empty] | Estimate | Permit & Fees | Owner Contingency | TOTAL COST | TOTAL COST (20% Increase)
| Type | Priority |  | Name | Description |  | 3% | 10% | (2017 $) | (2021 $)
1 | Plumbing System | 1 | Urgent (1 Year) | Investigate Shower Drainage Issues in Dorm Bathroom | Current chief reported shower drains in both dorm bathrooms were not draining properly causing backup into building. Recommend investigation by plumbing professional to determine cause and/or solution. | 504 | 15 | 50 | 570 | 2000
[9 empty] | Urgent (Immediate) | 0
[9 empty] | Urgent (1 Year) | 2000
[9 empty] | Urgent (2-3 Years) | 0
[9 empty] | Near Term (4-7 Years) | 0
[9 empty] | GRAND TOTALS | 2000

## Wendell 2
FACILITY CONDITION ASSESSMENTS
274 Wendell Station #2
# | Deficiency Information |  |  |  |  | Full Deficiency Cost Estimate
[6 empty] | Estimate | Permit & Fees | Owner Contingency | TOTAL COST | TOTAL COST (20% Increase)
| Type | Priority |  | Name | Description |  | 3% | 10% | (2017 $) | (2021 $)
1 | Electrical System | 1 | Urgent (1 Year) | Add Monitoring to Fire Alarm Panel | The existing fire alarm system is not monitored. Add (2) phone lines to panel for monitoring. | 1000 | 30 | 100 | 1130 | 1356
2 | Site Infrastructure | 1 | Urgent (1 Year) | EMS - Repair Cracks, Seal Coat, and Restripe Existing Parking Lot | Recommend repairing cracks and seal coating the existing surface to prolong lifetime of parking area. | 2550 | 77 | 255 | 2882 | 3458.4
3 | Site Infrastructure | 1 | Urgent (1 Year) | Fire Station - Repair Cracks, Seal Coat, and Restripe Existing Parking Lot | Recommend repairing cracks and seal coating the existing surface to prolong lifetime of parking area. | 2775 | 83 | 278 | 3136 | 3763.2
4 | Mechanical System | 5 | Near Term (4-7 Years) | DX Split System 2 - Addition Renewal | Auto generated renewal for DX Split System 2 - Addition. System Description: Outdoor condensing unit: 3.5 Tons. Model # 4TTR4042A10000AA; Serial # 7211M7L2F. Cooling Coil: 3.5 Tons. Model # 4TXCB042BC3HCAA; Serial # 7235BY8SG. Gas-Fired Furnace: est. 1400 CFM. Model No. XR90. | 7037 | 211 | 704 | 7952 | 9542.4
5 | Mechanical System | 5 | Near Term (4-7 Years) | EMS Vehicle Bay Unit Heater- Gas Fired Renewal | Auto generated renewal for Vehicle Bay Unit Heaters - Gas Fired. Heating for the vehicle bay is provided by a suspended unit heater, capacity of 100,000 BTUH. | 2756 | 83 | 276 | 3115 | 3738
6 | Architectural | 5 | Near Term (4-7 Years) | Install Fluid Applied Roof Coating | 29 y.o. economy PEMB metal roof system on building is exhibiting signs of fastener neoprene washer failure. Also reported issues of leaks at new/old roof intersection. Recommend installation of fluid applied roof coating to extend the life of original roof area. | 38016 | 1140 | 3802 | 42958 | 51549.6
7 | Site Infrastructure | 6 | Near Term (4-7 Years) | Fire Station - Asphalt Parking Lot - Typical Fire Station Renewal | Auto generated renewal for Fire Station - Asphalt Parking Lot - Typical Fire Station. | 14875 | 446 | 1488 | 16809 | 20170.8
[9 empty] | Urgent (Immediate) | 0
[9 empty] | Urgent (1 Year) | 8577.6
[9 empty] | Urgent (2-3 Years) | 0
[9 empty] | Near Term (4-7 Years) | 85000.8
[9 empty] | GRAND TOTALS | 93578.4

## Western Wake
FACILITY CONDITION ASSESSMENTS
164 Western Wake Station #1
# | Deficiency Information |  |  |  |  | Full Deficiency Cost Estimate
[6 empty] | Estimate | Permit & Fees | Owner Contingency | TOTAL COST | TOTAL COST (20% Increase)
| Type | Priority |  | Name | Description |  | 3% | 10% | (2017 $) | (2021 $)
1 | Site Infrastructure | 1 | Urgent (1 Year) | Repair Paving Failure at South Rear Entry | Repair Paving Failure at South Rear Entry | 1071 | 32 | 107 | 1210 | 1452
2 | Site Infrastructure | 1 | Urgent (1 Year) | Replace 5 Sections of Concrete Sidewalk at South Door | Replace 5 Sections of Concrete Sidewalk at South Door for Accessibility | 1506 | 45 | 151 | 1702 | 2042.4
3 | Plumbing System | 3 | Urgent (2-3 Years) | Mens Restroom Fixtures Renewal | Auto generated renewal for Mens Restroom Fixtures. System Description: Includes 2 water closets, 1 vitreous china wall mounted lavatory, 1 vitreous china urinal, and 1 tile shower. | 5313 | 159 | 531 | 6003 | 7203.6
4 | Plumbing System | 3 | Urgent (2-3 Years) | Womens Restroom Fixtures Renewal | Auto generated renewal for Womens Restroom Fixtures. System Description: Includes 2 water closets, 2 vitreous china wall mounted lavatories and 1 tile shower. | 6080 | 182 | 608 | 6870 | 8244
5 | Site Infrastructure | 4 | Near Term (4-7 Years) | Repair Cracks, Seal Coat, and Restripe Existing Parking Lot | Recommend repairing cracks and seal coating the existing surface to prolong lifetime of parking area. | 11000 | 330 | 1100 | 12430 | 14916
6 | Architectural Aesthetics | 4 | Near Term (4-7 Years) | Re-caulk Masonry Expansion Joints | Masonry expansion joint material is brittle and cracking. | 2800 | 84 | 280 | 3164 | 3796.8
[9 empty] | Urgent (Immediate) | 0
[9 empty] | Urgent (1 Year) | 3494.4
[9 empty] | Urgent (2-3 Years) | 15447.6
[9 empty] | Near Term (4-7 Years) | 18712.8
[9 empty] | GRAND TOTALS | 37654.8